CARTERTON DISTRICT COUNCIL

TRADE WASTE BYLAW 2008

1	INTRODUCTION

This bylaw regulates the discharge of Trade Waste to a Sewerage System operated by Carterton District Council a Wastewater Authority.

- Section (s.) 158 of the Local Government Act (LGA) requires regular review of all bylaws.

- 1.1 	Commencement and application

This bylaw comes into force on 1st July 2008……………….

- 1.2	Revocation

Not applicable

- 1.3	Scope of the bylaw

1.3.1

The bylaw provides for the:

(a) Acceptance of long-term, intermittent, or Temporary Discharge of Trade Waste to the Sewerage 
	System;

(b) Establishment of three grades of Trade Waste: Permitted, Conditional and Prohibited; 
(c) Evaluation of individual Trade Waste discharges to be against specified criteria; 
(d) Correct storage of materials in order to protect the Sewerage System from spillage;

(e) Installation of flow meters, samplers or other devices to measure flow and quality of the Trade Waste 
	discharge;

(f)  Pre-treatment of waste before it is accepted for discharge to the Sewerage System;

(g) Sampling and monitoring of Trade Waste discharges to ensure compliance with the bylaw; (h) WWA to accept or refuse a Trade Waste discharge;

(i)  Charges to be set to cover the cost of conveying, treating and disposing of, or reusing, Trade Waste 
	and the associated costs of administration and monitoring;

(j)  Administrative mechanisms for the operation of the bylaw; and

(k) Establishment of waste minimization and management programmes (including sludges) for Trade 
	Waste producers.

9

1.3.2 	Compliance with other Acts

Nothing in this bylaw shall derogate from any of the provisions of the Health Act, the Health and Safety in Employment Act, the Resource Management Act, the Building Act, the Hazardous Substances and New Organisms Act and its regulations or any other relevant statutory or regulatory requirements.  In the event of any inconsistency between legislation the more stringent requirement applies.

1.3.3 	Trade premises and other users to which the bylaw applies

This bylaw shall apply to all Trade Premises within the Carterton District where Trade Wastes are discharged or sought or likely to be discharged to the Sewerage System operated by the WWA or its agents.   The bylaw shall also apply to Tankered Wastes collected for the purpose of discharge to the Sewerage Systems operated by the WWA or its agents.

Pursuant to s. 196 of the Local Government Act the WWA may refuse to accept any type of Trade Waste which is not in accordance with this bylaw.

1.4	Referenced documents

- New Zealand Standards

NZS 4304:2002	Management of healthcare waste

NZS 5465:2001	Self containment for motor caravans and caravans

NZS 9201:- - - -	Model general bylaws

Part 22:1999	Wastewater drainage

- Joint Australian/New Zealand Standards

- AS/NZS 5667:- - - -

- Part 1:1998

- Part 10:1998

- British Standards

BS 3680:- - - -

Part 11A:1992

Part 11B:1992

- BS 5728:- - - -

- Part 3:1997

- BS 6068: - - - -

Part 6:- - - -

Section 6.10:1993

BS EN 25667-1: 1994 BS 6068-6.1:1981

BS EN 25667-2: 1993 BS 6068-6.2:1991

BS EN 5667-3: 2003 BS 6068-6.3:2003

Water quality - Sampling

Guidance on the design of sampling programs, sampling techniques and the preservation and handling of samples

Guidance on sampling of waste waters

Measurement of liquid flow in open channels

Free surface flow in closed conduits - Methods of measurement 
Free surface flow in closed conduits  - Specification for performance and 
installation of equipment for measurement of free surface flow in closed conduits

Measurement of flow of cold potable water in closed conduits 
Methods for determining principal characteristics of single mechanical water meters (including test equipment)

- Water quality

Sampling

Guidance on sampling of waste waters

Water quality. Sampling. Guidance on the design of sampling programmes

Water quality. Sampling. Guidance on sampling techniques

Water quality. Sampling. Guidance on the preservation and handling of water samples

10

- New Zealand Legislation

Building Act 2004

Hazardous Substances and New Organisms Act (HSNO) 1996 and associated Regulations Health Act 1956

- Health and Safety in Employment Act 1992

Land Transport Rule Dangerous Goods 1999 Rule 45001 Local Government Act (LGA) 2002

- Resource Management Act (RMA) 1991 and associated Regulations

Other Publications

Agricultural and Resource Management Council of Australia and New Zealand  (ARMCANZ) and Australia New Zealand Environment and Conservation Council (ANZECC)

Guidelines for Sewerage Systems: Acceptance of Trade Wastes (industrial waste) 12 (1994) 
Document available from Australian Water Association (AWA)   www.awa.asn.au

American Water Works Association

Standard methods for the examination of water and wastewater 20th Edition (1999) 
Document available from American Water Works Association   www.awwa.org

Building Industry Authority

- New Zealand Building Code (NZBC) 1992 and Approved Documents

Document available from Building Industry Authority (BIA)   www.bia.govt.nz

Ministry for the Environment (MfE)

Landfill Acceptance Criteria (2004)

The New Zealand Waste Strategy (2002)

Documents available from Ministry for the Environment New Zealand   www.mfe.govt.nz

National Radiation Laboratory (NRL)

NRL C1 Code of safe practice for the use of unsealed radioactive materials (1996). 
Document available from National Radiation Laboratory   www.nrl.moh.govt.nz

New Zealand Water and Wastes Association (NZWWA)

Guidelines for the Safe Application of Biosolids to Land in New Zealand (2003) Liquid and Hazardous Wastes Code of Practice (2003)

Documents available from New Zealand Water & Wastes Association (NZWWA)   www.nzwwa.org.nz

New Zealand Water Environment Research Foundation (NZWERF)

New Zealand Municipal Wastewater Monitoring Guidelines (2002)

Document  available  from  New  Zealand  Water  Environment  Research  Foundation  (NZWERF) 
www.nzwerf.org

Sydney Water Corporation 
Trade Waste Policy (2004)

Document available from Sydney Water Corporation   www.sydneywater.com.au

United States Environment Protection Agency (US EPA)

Method 9095A Paint Filter Liquids Test (1996)

Document available from United States Environmental Protection Agency www.epa.gov

1.5	Definitions

For the purposes of this bylaw the following definitions shall apply:

ACCESS POINT is a place where access may be made to a Private Drain for inspection (including sampling or measurement), cleaning or maintenance. The location of the Access Point shall be in accordance with the New Zealand Building Code.

11

- ANALYST means a testing laboratory Approved in writing by an Authorized Officer on behalf of the WWA.

APPROVAL or APPROVED means Approval or Approved in writing by the Wastewater Authority (WWA), either by resolution of the Council or by an Authorized Officer.

AUTHORIZED OFFICER means any officer appointed by the Territorial Authority (TA) as an enforcement officer under s. 177 of the Local Government Act 2002 as an enforcement officer with powers of entry as prescribed by sections (s. s) 171-174.

BIOSOLIDS means Sewage Sludge derived from a Sewage treatment plant that has been treated and/ 
or stabilized to the extent that it is able to be safely and beneficially applied to land and does not include 
products derived solely from industrial wastewater treatment plants.  The term Biosolid/Biosolids is used 
generically throughout this document to include products containing Biosolids (e.g. composts).

CHARACTERISTIC means any of the physical or chemical Characteristics of a Trade Waste and may include the level of a characteristic.

CLEANER PRODUCTION means the implementation on Trade Premises, of effective operations, methods and processes appropriate to the goal of reducing or eliminating the quantity and toxicity of wastes.   This is required to minimize and manage Trade Waste by:

(a) Using energy and resources efficiently, avoiding or reducing the amount of wastes produced; (b) Producing environmentally sound products and services;

(c) Achieving less waste, fewer costs and higher profits.

CONDENSING WATER or COOLING WATER means any water used in any trade, industry, or commercial process or operation in such a manner that it does not take up matter into solution or suspension.

CONDITIONAL TRADE WASTE means Trade Waste which has conditions placed upon the Consent Holder by the WWA.

CONSENT means a Consent in writing given by the WWA and signed by an Authorized Officer authorizing a Person to discharge Trade Wastes to the Sewerage System.

CONSENT HOLDER means the Person occupying Trade Premises who has obtained a Consent to discharge or direct the manner of discharge of Trade Waste from any Premises to the WWA’s Sewerage System, and includes any Person who does any act on behalf or with the express or implied Consent of the Consent Holder (whether for reward or not) and any licensee of the Consent Holder.

CONTAMINANT includes any substance (including gases, odorous compounds, liquids, solids and micro-organisms) or energy (excluding noise) or heat, that either by itself or in combination with the same, similar, or other substances, energy or heat -

(a) When discharged into water, changes or is likely to change the physical, chemical, or biological 
	condition of water; or

(b) When discharged onto or into land or into air, changes or is likely to change the physical, chemical, 
	or biological condition of the land or air onto or into which it is discharged;

or as described or contained in the Resource Management Act.

12

CONTINGENCY MANAGEMENT PROCEDURES means those procedures developed and used to avoid, remedy, or mitigate the actual and/or potential adverse effects of these activities on the environment from an unexpected or unscheduled event resulting in discharge, or potential discharge of Contaminants of concern into the Sewerage System.

COUNCIL means the Carterton District Council.

DISCONNECTION means the physical cutting and sealing of any of the Wastewater Authority’s water services, utilities, drains or Sewer for use by any Person.

DISTRICT means the district of the Territorial Authority established under the LGA which has adopted this bylaw.

DOMESTIC SEWAGE means Foul Water (with or without matter in solution or suspension therein) discharged from Premises used solely for residential purposes, or wastes of the same character discharged from other Premises; but does not include any solids, liquids, or gases that may not lawfully be discharged into the Sewerage System and may include geothermal water.

FOUL WATER means the discharge from any sanitary fixtures (any fixture which is intended to be used for sanitation - the term used to describe activities of washing and/or excretion carried out in a manner or condition such that the effect on health is minimized, with regard to dirt and infection) or sanitary appliance (an appliance which is intended to be used for sanitation which is not a sanitary fixture -
included are machines for washing dishes and clothes).

HAZARDOUS WASTES means hazardous substances as defined by the Hazardous Substances and New Organisms Act 1996.

- INFRINGEMENT means an offence as specified by this bylaw under s. s 243 and 259 of the LGA.

LONG TERM COUNCIL COMMUNITY PLAN (LTCCP) means a long term council community plan adopted under s. 93 of the LGA.

MANAGEMENT PLAN means the plan for management of operations on the Premises from which Trade Wastes come, and may include provision for Cleaner Production, waste minimization, discharge, Contingency Management Procedures, and any relevant industry Code of Practice.

MASS LIMIT means the total mass of any characteristic that may be discharged to the Wastewater Authority Sewerage System over any stated period from any single Point of Discharge or collectively from several points of discharge.

MAXIMUM CONCENTRATION means the instantaneous peak concentration that may be discharged at any instant in time.

- OCCUPIER means the Person occupying Trade Premises connected to the Sewerage System.

PERMITTED DISCHARGE means a Trade Waste discharge that has been approved by, or is acceptable 
to, the Wastewater Authority and as long as it has the physical and chemical Characteristics which comply 
with the requirements of the Wastewater Authority standard as defined in Schedule 1A of this bylaw.

- PERSON includes a corporation sole and also a body of Persons whether incorporated or unincorporated.

POINT OF DISCHARGE is the boundary between the public Sewer and a Private Drain but for the 
purposes of monitoring, sampling and testing, shall be as designated in the Trade Waste Consent.

13

PRE-TREATMENT means any processing of Trade Waste designed to reduce or vary any characteristic 
in a waste before discharge to the Sewerage System in order to comply with a Trade Waste Consent.

PREMISES means either:

(a) A property or allotment which is held under a separate certificate of title or for which a separate 
	certificate of title may be issued and in respect to which a building consent has been or may be issued; 
	or

(b) A building that has been defined as an individual unit by a cross-lease, unit title or company lease 
	and for which a certificate of title is available; or

(c) Land held in public ownership (e.g. reserve) for a particular purpose; or

(d) Individual units in buildings which are separately leased or separately occupied.

PRIVATE DRAIN means that section of drain between the Premises and the point of connection to the Wastewater Authority’s Sewerage System.

PROHIBITED TRADE WASTES means a Trade Waste that has prohibited Characteristics as defined in 
Schedule 1B and does not meet the conditions of Schedule 1A.  The waste is not acceptable for discharge 
into the Wastewater Authority’s system unless specifically approved by them as a Conditional Trade 
Waste.

SCHEDULE OF RATES AND CHARGES means the list of items, terms and prices for services associated with the discharge of Trade Waste as approved by the Wastewater Authority.

- SEWAGE means Foul Water and may include Trade Wastes.

SEWAGE SLUDGE means the material settled out and removed from Sewage during the treatment process.

- SEWER means the pipe work drainage system that conveys Sewage.

SEWERAGE SYSTEM means the collection, treatment and disposal of Sewage and Trade Wastes, 
including all sewers, pumping stations, storage tanks, Sewage treatment plants, outfalls, and other 
related structures operated by the WWA and used for the reception, treatment and disposal of Trade 
Wastes.

SIGNIFICANT INDUSTRY is a term to indicate the relative size of a given industry compared to the 
capacity of the Sewerage System (including Sewage treatment plant) which services that industry. 
Industry size relates to volume and/or loads discharging into the Sewerage System.  Loads can be the 
conventional loadings of BOD5 and SS or some other particular Contaminant (e.g. boron, chromium) 
which will have an effect or the propensity to have an effect on the sizing of the Sewerage System, the 
on-going system operation and/or the quality of the treated effluent that is discharged.

- STORMWATER means surface water run-off resulting from precipitation.

TANKERED WASTE is water or other liquid, including waste matter in solution or suspension, which is conveyed by vehicle for disposal, excluding Domestic Sewage discharged directly from house buses, caravans, buses and similar vehicles.

14

TEMPORARY DISCHARGE means any discharge of an intermittent or short duration.  Such discharges 
include the short-term discharge of an unusual waste from Premises subject to an existing Consent.

- TERRITORIAL AUTHORITY (TA) means a city council or district council.

TRADE PREMISES means:

(a) Any Premises used or intended to be used for any industrial or trade purpose; or

(b) Any Premises used or intended to be used for the storage, transfer, treatment, or disposal of waste 
	materials or for other waste management purposes, or used for composting organic materials; or

(c) Any other Premises from which a Contaminant is discharged in connection with any industrial or trade 
	process;

(d) Any other Premises discharging other than Domestic Sewage;

and includes any land or Premises wholly or mainly used for agricultural or horticultural purposes.

TRADE WASTE is any liquid, with or without matter in suspension or solution, that is or may be discharged from a Trade Premises to the WWA’s Sewerage System in the course of any trade or industrial process or operation, or in the course of any activity or operation of a like nature; and may include Condensing or Cooling waters; Stormwater which cannot be practically separated, or Domestic Sewage.

WASTEWATER AUTHORITY (WWA) means the unit of a TA including its authorized agents, responsible for the collection, treatment and disposal of Sewage.

WORKING DAY means any day of the week other than:

(a) A Saturday, a Sunday, Waitangi Day, Good Friday, Easter Monday, Anzac Day, the Sovereign’s 
	birthday, Labour Day; and

(b) A day in the period commencing with the 25th day of December in a year and ending with the 2nd 
	day of January in the following year.

1.6	Abbreviations

$/kg	dollars per kilogram

$/L/s	dollars per litre per second

$/m3	dollars per cubic metre

oC	degrees Celsius

ANZECC    Australian New Zealand Environment and Conservation Council

B	boron

BOD5	Biochemical Oxygen Demand

Br2	bromine

Cl2	chlorine

CN	cyanide

COD	Chemical Oxygen Demand

DAF	dissolved air floatation

DP	deposited plan

DS	dry solids

F	fluoride

FOGs	fats, oils and greases

15

g/m3	grams per cubic metre

GST	goods and services tax

H2S	hydrogen sulphide

HAHs	halogenated aromatic hydrocarbons

HCHO	formaldehyde

HCN	hydrogen cyanide

hr	hour

HSNO	Hazardous Substances and New Organisms Act

kg/day	kilogram per day

L	litre

L/s	litre per second

LGA	Local Government Act

LTCCP	long term council community plan

m3	cubic metre

max.	maximum

MBAS	methylene blue active substances

MfE	Ministry for the Environment

mg/L	milligram per litre

mL/L	millilitre per litre

mm	millimetres

MSDS	material safety data sheets

N	nitrogen

NH3	ammonia

NH3-N	ammoniacal nitrogen

P	phosphorus

PAHs	polycyclic (or polynuclear) aromatic hydrocarbons

PBBs	polybrominated biphenyls

PCBs	polychlorinated biphenyls

pH	measure of acidity/alkalinity

RMA	Resource Management Act

s	second

s.	section

s. s	sections

SBR	sequencing batch reactor

SO4	sulphate

SS	suspended solids concentration

TAs	territorial authorities

UV	ultra violet

UVT	ultra violet transmission

WC	water closet

WWA	wastewater authority

1.7	General

1.7.1

In this bylaw one gender includes all genders, the singular includes the plural, and the plural includes the 
singular.

1.7.2

The word “shall” identifies a mandatory requirement for compliance with the Standard.  The word “should” refers to practices which are advised or recommended.

16

1.7.3

The term “normative” has been used in this Standard to define the application of the Appendix to which it applies.   A “normative” Appendix is an integral part of a Standard.

1.7.4

Clauses prefixed by "C" and printed in italic type inside a grey screen are intended as comments on the 
corresponding mandatory clauses.  They are not to be taken as the only or complete interpretation of the 
corresponding clause, nor should they be used for determining in any way the mandatory requirements 
of compliance within this Standard.   The Standard can be complied with if the comment is ignored.

17

2	COMPLIANCE WITH THE BYLAW

2.1	Control of discharges

2.1.1

No Person shall:

(a) Discharge, or allow to be discharged, any Trade Waste to the Sewerage System except in 
	accordance with the provisions of this bylaw;

(b) Discharge, or allow to be discharged, a Prohibited Trade Waste into the Sewerage System;

(c) Add or permit the addition of Condensing or Cooling Water to any Trade Waste which discharges into 
	the Sewerage System unless specific Approval is given in a Consent; or

(d) Add or permit the addition of Stormwater to any Trade Waste which discharges into the Sewerage 
	System unless specific Approval is given in a Consent.

2.1.2

In the event of failure to comply with 2.1.1 (a) - (d) the WWA may physically prevent discharge to the 
Sewerage System if a reasonable alternative action cannot be established with the discharging party or 
parties.

2.1.3

Any Person discharging to the WWA Sewerage System shall also comply with requirements of the Hazardous Substances and New Organisms (HSNO) Act and the RMA.

2.2 	Storage, transport, handling and use of hazardous or harmful materials

(a) All Persons on Trade Premises shall take all reasonable steps to prevent the accidental entry of any 
	of the materials listed in 2.2(c) of this bylaw from entry into the Sewerage System as a result of 
	leakage, spillage or other mishap.

(b) No Person shall store, transport, handle or use, or cause to be stored, transported, handled or used 
	any hazardous substance as defined by HSNO or any of the materials listed in 2.2(c) in a manner 
	that may cause the material to enter the Sewerage System and cause harmful effects.

(c) Materials referred to in 2.2 (a) and (b) are those:

(i)	Products or wastes containing corrosive, toxic, biocidal, radioactive, flammable or explosive

materials

(ii) 	Likely to generate toxic, flammable, explosive or corrosive materials in quantities likely to be

hazardous, when mixed with the wastewater stream

(iii)  Likely to be deleterious to the health and safety of the WWA’s staff, Approved contractors and 
	the public or be harmful to the Sewerage System.

18

3	TRADE WASTE DISCHARGES AND CONSENTS

3.1	Classification of trade waste discharges

3.1.1

Trade Waste discharges shall be classified as one of the following types:

(a) Permitted (Consent required if decided by the WWA);

(b) Conditional (Consent required); or

(c) Prohibited (not Consentable).

3.1.2

The WWA is not obliged to accept any Trade Waste.  No application for a Trade Waste Consent shall be Approved where the Trade Waste discharge would contain, or is likely to contain, Characteristics which are Prohibited.

3.1.3

No Person shall discharge, or cause to be discharged, any Trade Waste to the WWA Sewer except in accordance with the provisions of this bylaw.

3.2	Application for a trade waste consent

3.2.1	Formal application

Every Person who does, proposes to, or is likely to:

(a) Discharge into the Sewerage System any Trade Waste (either continuously, intermittently or 
	temporarily); or

(b) Vary the Characteristics of a Consent to discharge that has previously been granted; or

- (c) Vary the conditions of Consent to discharge that has previously been granted; or

(d) Significantly change the method or means of Pre-treatment for discharge under an existing Consent 
	shall if required by the WWA to complete an application in the prescribed form for the Consent of the 
	WWA (see Appendix A), to the discharge of that Trade Waste, or to the proposed variations.

3.2.2

The WWA reserves the right to deal with the owner as well as the Occupier of any Trade Premises.

3.2.3

Where the Trade Premises produces Trade Waste from more than one area, a separate copy of the “Description of Trade Waste and Premises” (see Appendix B) shall be included in any application for Trade Waste discharge for each area. This applies whether or not the separate areas are part of a single or separate trade process.

3.2.4

The applicant shall ensure that the application and every other document conveying required information 
is properly executed and any act done for, or on behalf of, the eventual Consent Holder (whether for 
reward or not) in making any such application shall be deemed to be an act of the Consent Holder.

19

3.2.5

The WWA may require an application to be supported by an independent report/statement completed by a suitably experienced and external auditor to verify any or all information supplied by the applicant, and this may include a Management Plan.

3.2.6

Every application shall be accompanied by a Trade Waste application fee in accordance with the WWA’s Schedule of Rates and Charges.

3.3 	Processing of an application

The WWA shall acknowledge the application in writing within 10 Working Days of the receipt of the application.

3.4	Information and analysis

3.4.1

On the receipt of any application for a Trade Waste Consent to discharge from any Premises or to alter an existing discharge, the WWA may:

(a) Require the applicant to submit any additional information which it considers necessary to reach an 
	informed decision;

(b) Require the applicant to submit a Management Plan to the satisfaction of the WWA;

(c) Whenever appropriate have the discharge investigated and analysed as provided for in 5.1 and 5.3 
	of this bylaw.

3.4.2

The WWA shall notify the applicant of any requirement under this clause within 10 Working Days of receipt of the application.

3.5 	Consideration of an application

Within 15 Working Days (or extended as necessary by the WWA) of receipt of an application complying with this bylaw and/or all requirements under 3.4, whichever is the later, the WWA shall, after considering the matters in 3.6 action one of the following in writing:

(a) Grant the application as a Permitted Trade Waste and inform the applicant of the decision by issuing 
	the appropriate notice;

(b) Grant the application as a Conditional Trade Waste discharge Consent and inform the applicant of 
	the decision and the conditions imposed on the discharge by issuing the appropriate notice of 
	Consent to the discharge; or

(c) Decline the application and notify the applicant of the decision giving a statement of the reasons for 
	refusal.

20

3.6	Consideration criteria

In considering any application for a Trade Waste Consent to discharge from any Trade Premises or Tankered Waste into the Sewerage System and in imposing any conditions on such a Consent, the WWA shall take into consideration the quality, volume, and rate of discharge of the Trade Waste from such Premises or tanker in relation to:

(a) The health and safety of WWA staff, Council’s agents and the public;

(b) The limits and/or maximum values for Characteristics of Trade Waste as specified in Schedules 1A 
	and 1B of this bylaw;

(c) The extent to which the Trade Waste may react with other Trade Waste or Foul Water to produce 
	an undesirable effect, e.g. settlement of solids, production of odours, accelerated corrosion and 
	deterioration of the Sewerage System etc.;

(d) The flows and velocities in the Sewer, or Sewers and the material or construction of the Sewer or 
	Sewers;

(e) The capacity of the Sewer or Sewers and the capacity of any Sewage treatment works, and other 
	facilities;

(f)	The nature of any Sewage treatment process and the degree to which the Trade Waste is capable

of being treated in the Sewage treatment works;

(g) The timing and balancing of flows into the Sewerage System;

(h) Any statutory requirements relating to the discharge of raw or treated wastewater to receiving waters, 
	the disposal of Sewage Sludges, beneficial use of Biosolids, and any discharge to air, (including the 
	necessity for compliance with any resource consent, discharge permit or water classification);

(i)	The effect of the Trade Waste discharge on the ultimate receiving environment;

(j)	The conditions on resource consents for the Sewerage System and the residuals from it;

(k) The possibility of unscheduled, unexpected or accidental events and the degree of risk these could 
	cause to humans, the Sewerage System and the environment;

(l) 	Consideration for other existing or future discharges; 
(m) Amenability of the Trade Waste to Pre-treatment;

(n) Existing Pre-treatment works on the Premises and the potential for their future use; (o) Cleaner Production techniques and waste minimization practices; 
(p) Requirements and limitations related to Sewage Sludge disposal and reuse; 
(q) Control of Stormwater;

(r) Management Plan; and

(s) Tankered Waste being discharged at an Approved location/s.

21

3.7 	Conditions of trade waste consent

Any Trade Waste Consent to discharge may be granted subject to such conditions that the WWA may impose, including but not limited to:

(a) The particular public Sewer or Sewers to which the discharge will be made;

(b) The maximum daily volume of the discharge and the maximum rate of discharge, and the duration 
	of maximum discharge;

(c) The maximum limit or permissible range of any specified Characteristics of the discharge, including 
	concentrations and/or Mass Limits determined in accordance with 3.8;

(d) The period or periods of the day during which the discharge, or a particular concentration, or volume 
	of discharge may be made;

(e) The degree of acidity, or alkalinity of the discharge at the time of discharge; (f) The temperature of the Trade Waste at the time of discharge;

(g) The provision by, or for the Consent Holder, at the Consent Holder’s expense, of screens, grease 
	traps, silt traps or other Pre-treatment works to control Trade Waste discharge Characteristics to the 
	consented levels;

(h) The provision and maintenance at the Consent Holder’s expense of inspection chambers, manholes 
	or other apparatus or devices to provide reasonable access to drains for sampling and inspection;

(i)	The provision and maintenance of a sampling, analysis and testing programme and flow measurement

requirements, at the Consent Holder’s expense;

(j) 	The method or methods to be used for the measuring flow rates and/or volume and taking samples 
	of the discharge for use in determining the amount of any Trade Waste charges applicable to that 
	discharge;

(k) The provision and maintenance by, and at the expense of, the Consent Holder of such meters or 
	devices as may be required to measure the volume or flow rate of any Trade Waste being discharged 
	from the Premises, and for the testing of such meters;

(l) 	The provision and maintenance, at the Consent Holder’s expense of such services, (whether 
	electricity, water or compressed air or otherwise), which may be required, in order to operate meters 
	and similar devices;

(m) At times specified, the provision in a WWA Approved format by the Consent Holder to the WWA of 
	all flow and/or volume records and results of analyses (including Pre-treatment by-products e.g. 
	Sewage Sludge disposal);

(n) The provision and implementation of a Management Plan;

(o) Risk assessment of damage to the environment due to an accidental discharge of a chemical;

(p) Waste minimization and management;

(q) Cleaner Production techniques;

22

(r) Remote control of discharges;

(s) Third party treatment, carriage, discharge or disposal of by-products of Pre-treatment of Trade Waste 
	(including Sewage Sludge disposal);

(t)  Requirement to provide a bond or insurance in favour of the WWA where failure to comply with the 
	Consent could result in damage to the WWA’s Sewerage System, its treatment plants, or could result 
	in the WWA being in breach of any statutory obligation; and

(u) Remote monitoring of discharges.

3.8	Duration

3.8.1	Permitted discharges

Permitted Discharges shall remain in force indefinitely until either:

(a) Cancellation under 2.1.2 or 3.10;

(b) The quantity and nature of the discharge changes significantly.   For a temporary discharge see 
	Appendix C;

(c) If in the opinion of the WWA the discharge changes or is likely to change to such an extent that it 
	becomes a Conditional or Prohibited Trade Waste;

(d) The WWA changes the Trade Waste management procedures by implementation of changed Trade 
	Waste Bylaw conditions or any amendment to, or replacement of, its Trade Waste Bylaw; or

(e) The conditions on resource consents for the Sewerage System and the residuals from it change.

In all cases, after appropriate consultation, the Person shall apply within 10 Working Days of this change occurring for a conditional Consent, in accordance with 3.2 of this bylaw.   This application shall be Approved prior to the occurrence of any new discharge.

3.8.2 	Conditional consents

Subject to 3.10 and 6.1 conditional Consents under this bylaw shall expire at the end of a term fixed by the WWA subject to the following:

(a) Conditional Consents may be given for a term not exceeding five years to a Consent Holder who at 
	the time of application satisfies the WWA that:

(i) 	The nature of the trade activity, or the process design and/or management of the Premises are

such that the Consent Holder has a demonstrated ability to meet the conditions of the Consent during its term; and/or

(ii) 	Cleaner Production techniques are successfully being utilized, or that a responsible investment

in Cleaner Production equipment or techniques is being made; and/or

(iii)  Significant investment in Pre-treatment facilities has been made, such that a longer period of 
	certainty for the amortizing of this investment is considered reasonable; and/or

(iv)  The reissuing of a Consent can not be unreasonably withheld.	➤

23

Notwithstanding the above the WWA retains the right to review the conditions at an earlier time.  The reasons for such an earlier review could include:

(A)  The level of Consent Holder compliance, including any accidents including spills or process 
	mishaps.

(B)  Matters pertaining to the WWA’s resource consents for the Sewerage System. (C) Matters pertaining to the WWA’s environmental policies and outcomes. 
(D) New control and treatment technologies and processes. 
(E)  Any of the matters outlined in section 4.

(F)  Matters pertaining to the WWA’s legal obligations.

(b) In all other cases the term of a Conditional Trade Waste Consent should not exceed two years;

(c) In all cases where either the Consent Holder or the owner of the Premises changes, or there is a 
	change of use, a new application for a Conditional Trade Waste Consent shall be made.  It shall be 
	the responsibility of the Consent Holder to lodge the new application; and

(d) The conditions on resource consents for the Sewerage System and the residuals from it change.

3.9 	Technical review and variation

3.9.1

The WWA at any time may require a Person undertaking a Permitted Discharge to apply for a Consent in accordance with 3.8.1.

3.9.2

The WWA may at any time during the term of a Trade Waste Consent, by written notice to the Consent 
Holder (following a reasonable period of consultation), vary any condition to such an extent as the WWA 
considers necessary following a review of the technical issues considered when setting conditions of 
Consent.   This is due to new information becoming available or to meet any new resource consent 
imposed on the discharge from the WWA’s treatment plant, or with any other legal requirements imposed 
on the WWA.

3.9.3

A Consent Holder may at any time during the term of a Consent, by written application to the WWA, seek to vary any condition of Consent, as provided for in 3.7 of this bylaw.

3.10 	Cancellation of the right to discharge

3.10.1   Suspension or cancellation on notice

The WWA may suspend or cancel any Consent or right to discharge at any time following 20 Working 
Days’ (during which consultation has occurred) notice to the Consent Holder or Person discharging any 
Trade Waste:

(a) For the failure to comply with any condition of the Consent;

(b) For the failure to maintain effective control over the discharge;

24

(c) For the failure to limit in accordance with the requirements of a Consent the volume, nature, or 
	composition of Trade Waste being discharged;

(d) In the event of any negligence which, in the opinion of the WWA, threatens the safety of, or threatens 
	to cause damage to any part of the Sewer System or the treatment plant or threatens the health or 
	safety of any Person;

(e) If any occurrence happens that, in the opinion of the WWA, poses a serious threat to the environment;

(f)  In the event of any breach of a resource consent held by the Council issued under the Resource 
	Management Act 1991;

(g) Failure to provide and when appropriate update a Management Plan as required for a conditional 
	Consent;

(h) Failure to follow the Management Plan provisions at the time of an unexpected, unscheduled or 
	accidental occurrence;

(i)  Failure to pay any charges under this bylaw; or

(j)  If any other circumstances arise which, in the opinion of the WWA, render it necessary in the public 
	interest to cancel the right to discharge.

If any process changes require more than 20 Working Days, reasonable time may be given to comply with the Consent conditions.

3.10.2   Summary cancellation

Further to 3.10.1 any Trade Waste Consent or discharge may at any time be summarily cancelled by the 
WWA on giving to the Consent Holder or Person discharging written notice of summary cancellation if:

(a) They discharge any Prohibited substance;

(b) The WWA is lawfully directed to withdraw or otherwise to terminate the Consent summarily;

(c) They discharge any Trade Waste unlawfully;

(d) If the continuance of discharge is, in the opinion of the WWA, a threat to the environment or public 
	health; -

(e) If the continuance of discharge may, in the opinion of the WWA, result in a breach of a resource 
	Consent held by the WWA; or

(f)  In the opinion of the WWA the continuance of the discharge puts at risk the ability of the WWA to 
	comply with conditions of a resource Consent and/or requires identified additional treatment 
	measures or costs to seek to avoid a breach of any such resource Consent.

25

4	TRADE WASTE APPROVAL CRITERIA

4.1	Pre-treatment

The WWA may approve a Trade Waste discharge (see Appendix D for appropriate form) subject to the provision of appropriate Pre-treatment systems to enable the Person discharging to comply with the bylaw. Such Pre-treatment systems shall be provided, operated and maintained by the Person discharging at their expense.

Refuse or garbage grinders, and macerators shall not be used to dispose of solid waste from Trade Premises to the Sewerage System unless Approved by the WWA.

The Person discharging shall not, unless approved by the WWA, add or permit the addition of any potable, Condensing, Cooling Water or Stormwater to any Trade Waste stream in order to vary the level of any Characteristics of the waste.

NOTE - Condensing and Cooling Water should not be discharged as of right to a Stormwater drain or natural waterway without the Consent of the appropriate authority.

4.2	Mass limits

A Conditional Trade Waste Consent to discharge may impose controls on a Trade Waste discharge by specifying Mass Limits for any Characteristic.

Mass Limits may be imposed for any Characteristic. Any Characteristic permitted by Mass Limit shall also have its Maximum Concentration limited to the value scheduled unless Approved otherwise.

When setting Mass Limit allocations for a particular Characteristic the WWA shall consider:

(a) The operational requirements of and risk to the Sewerage System, and risks to occupational health 
	and safety, public health, and the ultimate receiving environment;

(b) Whether or not the levels proposed pose a threat to the planned or actual beneficial reuse of Biosolids 
	or Sewage Sludge;

(c) Conditions in the Sewerage System near the Trade Waste discharge point and elsewhere in the 
	Sewerage System;

(d) The extent to which the available industrial capacity was used in the last financial period and is 
	expected to be used in the forthcoming period;

(e) Whether or not the applicant uses Cleaner Production techniques within a period satisfactory to the 
	WWA;

(f) 	Whether or not there is any net benefit to be gained by the increase of one Characteristic concurrently 
	with the decrease of another to justify any increased application for industrial capacity;

(g) Any requirements of the WWA to reduce the pollutant discharge of the Sewerage System;

(h) How great a proportion the mass flow of a Characteristic of the discharge will be of the total mass 
	flow of that Characteristic in the Sewerage System;

(i)	The total mass of the Characteristic allowable in the Sewerage System, and the proportion (if any)

to be reserved for future allocations; and

(j) 	Whether or not there is an interaction with other Characteristics which increases or decreases the 
	effect of either Characteristic on the Sewer reticulation, treatment process, or receiving water (or 
	land).

26

5	SAMPLING, TESTING AND MONITORING

5.1	Flow metering

5.1.1

Flow metering may be required by the WWA:

(a) On discharges when there is not a reasonable relationship between a metered water supply to the 
	Premises, and the discharge of Trade Waste;

(b) When the WWA will not approve a method of flow estimation; or

(c) When the discharge represents a significant proportion of the total flow/load received by the WWA.

5.1.2

The Consent Holder shall be responsible for the supply, installation, reading and maintenance of any 
meter required by the WWA for the measurement of the rate or quantity of discharge of Trade Waste. 
These devices shall be subject to the Approval of the WWA, but shall remain the property of the Consent 
Holder.

5.1.3

Records of flow and/or volume shall be available for viewing at any time by the WWA, and shall be 
submitted to the WWA at prescribed intervals by the Consent Holder in a format Approved by the WWA.

5.1.4

Meters shall be located in a position Approved by the WWA which provides the required degree of accuracy and should be readily accessible for reading and maintenance.  The meters shall be located in the correct position according to the manufacturer’s installation instructions.

5.1.5

The Consent Holder shall arrange for in situ calibration of the flow metering equipment and instrumentation 
by a Person and method Approved by the WWA upon installation and at least once a year thereafter to 
ensure its performance.  The meter accuracy should be 10 % but with no greater a deviation from the 
previous meter calibration of 5 %.  A copy of independent certification of each calibration result shall be 
submitted to the WWA.

5.1.6

Should any meter, after being calibrated, be found to have an error greater than that specified in 5.1.5 
as a repeatable measurement, the WWA may make an adjustment in accordance with the results shown 
by such tests back-dated for a period at the discretion of the WWA but not exceeding 12 months, and the 
Consent Holder shall pay or be credited a greater or lesser amount according to such adjustment.

5.2	Estimating discharge

5.2.1

Where no meter or similar apparatus is warranted, the WWA may require that a percentage of the water supplied to the Premises (or other such basis as seems reasonable) be used for estimating the rate or quantity of flow for the purposes of charging.

27

5.2.2

Should any meter be out of repair or cease to register, or be removed, the WWA shall estimate the discharge for the period since the previous reading of such meter, (based on the average of the previous 12 months charged to the Person discharging) and they shall pay according to such estimate.  Provided that when by reason of a large variation of discharge due to seasonal or other causes, the average of the previous 12 months would be an unreasonable estimate of the discharge, then the WWA may take into consideration other evidence for the purpose of arriving at a reasonable estimate, and the Person discharging shall pay according to such an estimate.

5.2.3

Where in the opinion of the WWA, a meter has been tampered with, the WWA (without prejudice to the 
other remedies available) may declare the reading void and estimate discharge as provided above.

5.3	Sampling and analysis

5.3.1

As determined by the WWA sampling, testing and monitoring may be undertaken to determine if:

(a) A discharge complies with the provisions of this bylaw;

(b) A discharge is to be classified as a Permitted, Conditional, or Prohibited, refer to 3.1;

(c) A discharge complies with the provisions of Schedule 1A for Permitted Discharge and any Consent 
	to discharge; and

(d) Trade Waste Consent charges are applicable to that discharge.

5.3.2

The taking, preservation, transportation and analysis of the sample shall be undertaken by an Authorized 
Officer or agent of the WWA, or the Person discharging in accordance with accepted industry standard 
methods, or by a method specifically Approved by the WWA.  The Person discharging shall be responsible 
for all reasonable costs.  Where a dispute arises as to the validity of the methods or procedures used for 
sampling or analysis, the dispute may be submitted to a mutually agreed independent arbitrator.

5.3.3

All Authorized Officers or authorized agents of the WWA, or any Analyst may enter any Premises believed to be discharging Trade Waste at any time in order to determine any Characteristics of any actual or potential discharge by:

(a) Taking readings and measurements; 
(b) Carrying out an inspection; and/or 
(c) Taking samples for testing,

of any solid, liquid, or gaseous material or any combination or mixture of such materials being discharged.

Authorization for entry to Premises is given under the LGA and entry shall be in compliance with the health and safety policies of that particular site.

28

5.4	Monitoring

5.4.1	Monitoring for compliance

The WWA is entitled to monitor and audit any Trade Waste discharge for compliance.   Whether for a 
Permitted Discharge or a conditional Consent discharge monitoring may be carried out as follows:

(a) The WWA or its authorized agent will take the sample and arrange for this sample to be analysed 
	in an Approved laboratory by agreed/approved analytical methods;

(b) The sampling procedure will be appropriate to the Trade Waste and the analysis;

(c) The WWA will audit the sampling and analysis carried out by a self-monitoring Trade Waste 
	discharger.   Analysis will be performed by an Approved laboratory.   Inter-laboratory checks are to 
	be part of this process;

(d) The WWA will audit the sampling and analysis carried out by an Analyst.  Analysis will be performed 
	by an Approved laboratory.   Inter-laboratory checks are to be part of this process; and

(e) The WWA will audit the Trade Waste Consent conditions including any Management Plans.

At the discretion of the WWA all costs of monitoring shall be met by the discharger either through direct payment to the laboratory or to the WWA.

5.4.2 	Sampling methodology

Normally a single grab or composite sample is sufficient. If required the grab or composite sample can be split equally into three as follows:

(a) One portion of the sample goes to the Trade Waste discharger for appropriate analysis and/or 
	storage;

(b) A second portion of the sample shall be analysed at a laboratory Approved by the WWA;

(c) A third portion of the sample is retained by the WWA for 20 Working Days, for additional analysis if 
	required.

Due consideration will be applied to any changes that could occur in retained Trade Waste samples and provisions to mitigate against changes will be adopted where practicable.

In all cases the samples shall be handled in an appropriate manner such that the Characteristics being tested for are, as far as reasonably possible, preserved.

All samples shall be preserved, handled, transported and delivered to an Approved laboratory according to best possible practice and Approved standards.

5.4.3 	Tankered wastes

Tankered Wastes shall not be discharged into the WWA’s Sewerage System by any Person or Consent Holder not compliant with the Liquid and Hazardous Wastes Code of Practice.

The WWA may accept Tankered Wastes for discharge at an Approved location.  Tankered Wastes shall:

(a) Be transported by a Consent Holder to discharge domestic septic tank or industrial wastes;

(b) Have material safety data sheets (MSDS) supplied to the WWA detailing the contents of a waste; 	➤

29

(c) Be tested to determine their character if the contents of the waste are not known.  Specialist advice 
	on Pre-treatment or acceptance may be required.  The cost of all testing and advice shall be borne 
	by the Consent Holder;

(d) Not be picked up and transported to the disposal site until appropriate arrangements and method for 
	disposal have been determined by the WWA;

(e) To prevent cross-contamination between tanker loads, the tanker shall be thoroughly washed prior 
	to collecting a load for disposal into the Sewerage System; and

(f)  Have 24 hours notice given for the disposal of wastes other than those sourced from domestic septic 
	tanks.

(g)  Be using the Waste Track system for the collection, transport, and disposal of all Tankered Waste

Any Person illegally disposing of, or causing to be disposed, Tankered Waste either by incorrect disclosure of contents (Characteristics and/or amount) or dumping into the WWA’s Sewerage System other than the prescribed location will be in breach of the bylaw.

5.4.4 	Disinfected/super chlorinated water

Any water used during the repair and construction of water mains shall be de-chlorinated prior to the 
discharge into the Sewerage System.   Application for a Temporary Discharge Consent shall be made. 
Such water shall not be disposed of to Stormwater or adjacent water courses without appropriate 
Approvals.

30

6	BYLAW ADMINISTRATION

6.1	Review of decisions

If any Person is dissatisfied with any decision by an Authorized Officer made under this bylaw, that Person may, by notice delivered to the Chief Executive Officer of the WWA not later than 20 Working Days after the decision by the Authorized Officer is served upon that Person, request the Chief Executive Officer to review any such decision and such a decision shall be final.

- Nothing in this clause shall affect any right of appeal under the LGA.

6.2 	Accidents and non-compliance

The Person discharging shall inform the WWA immediately on discovery of any accident including spills or process mishaps which may cause a breach of this bylaw.

In the event of any accident occurring when the Person holds a conditional Consent, then the WWA may review the Consent under 3.9 or may require the Consent Holder, within 20 Working Days of the date such requirement is notified to the Consent Holder in writing, to review the Contingency Management Procedures and re-submit for Approval the Management Plan with the WWA.

In the event of an accident occurring on the Premises of a Permitted Discharge, the WWA may require the Person discharging to apply for a conditional Consent.

6.3	Charges and payments

6.3.1	Charges

The WWA may recover fees and charges in accordance with the LGA.  Schedule 1C outlines a regime of possible charges.

6.3.2 	Invoicing

All charges determined in accordance with 6.3.1 shall be invoiced in accordance with WWA’s standard 
commercial practice.  The invoice shall provide each Person discharging with a copy of the information 
and calculations used to determine the extent of any charges and fees due, in regard to a discharge.

6.3.3 	Cease to discharge

The Person discharging shall be deemed to be continuing the discharge of Trade Waste and shall be liable for all charges, until notice of Disconnection is given.

6.3.4 	Failure to pay

All fees and charges payable under this bylaw shall be recoverable as a debt.  If the Person discharging fails to pay any fees and charges under this bylaw the WWA may cancel the right to discharge in accordance with 3.10.

6.3.5 	Recovery of costs

The WWA may recover costs under LGA relating to s. 150 and s. 151, wilful damage or negligent behaviour (s. 175) and remedying damage arising from breach of bylaw (s. 176).

31

6.4	Authorized officers

All Authorized Officers of the WWA, or other Persons authorized under s. 174 or s. 177 or paragraph 32 
of schedule 7 of the LGA, shall possess and produce on request warrants of authority and evidence of 
identity.

Any Authorized Officers may at any reasonable time enter any Premises believed to be discharging Trade Wastes to determine any Characteristic of any discharge by:

- (a) Taking readings and measurements; or

(b) Taking samples or any solids, liquids or gaseous material or any combination or mixtures of such 
	materials being discharged; or

(c) Observing accidental occurrences and clean-up.

The extent and level of delegation to Authorized Officers will be in accordance with the Council’s Register of Statutory Delegations and Warrants.

Authorization for entry to Premises is given under the LGA and entry shall be in compliance with the health and safety policies of that particular site.

6.5 	Transfer or termination of rights and responsibilities

6.5.1

A Trade Waste Consent to discharge shall be issued in the name of the given Consent Holder.   The Consent Holder shall not, unless written Approval is obtained from the WWA:

(a) Transfer to any other party the rights and responsibilities provided for under this bylaw, and under 
	the Consent;

(b) Allow a Point of Discharge to serve another Premises, or the Private Drain to that point to extend by 
	pipe or any other means to serve another Premises; or

(c) In particular and not in limitation of the above, allow Sewage from any other party to be discharged 
	at their Point of Discharge.

NOTE - This clause does not relate to Permitted Discharges.

6.5.2

Renewal of a Trade Waste Consent on change of ownership of Premises shall not be unreasonably withheld if the Characteristics of the Sewage remain unchanged.

- NOTE - This clause does not relate to Permitted Discharges.

6.5.3

The Person discharging shall give 48 hours notice in writing to the WWA of their requirement for 
Disconnection of the discharge connection and/or termination of the discharge Consent, except where 
demolition or relaying of the discharge drain is required, in which case the notice shall be within seven 
Working Days.  The Person discharging shall notify the WWA of the new address details for final invoicing.

On permanent Disconnection and/or termination the Person discharging may at the WWA’s discretion be liable for Trade Waste charges to the end of the current charging period.

32

6.5.4

When a Person discharging ceases to occupy Premises from which Trade Wastes are discharged into the Sewerage System any Consent granted shall terminate but without relieving the Person discharging from any obligations existing at the date of termination.

6.6	Service of documents

6.6.1	Delivery or post

Any notice or other document required to be given, served or delivered under this bylaw to a Person 
discharging may (in addition to any other method permitted by law) be given or served or delivered by 
being:

(a) Sent by pre-paid ordinary mail, courier, or facsimile, or email to the Person discharging at the Person 
	discharging last known place of residence or business;

(b) Sent by pre-paid ordinary mail, courier, or facsimile, or email to the Person discharging at any 
	address for service specified in a Consent to discharge;

(c) Where the Person discharging is a body corporate, sent by pre-paid ordinary mail, courier, or 
	facsimile, or email to, or left at its registered office; or

(d) Personally served on the Person discharging.

6.6.2 	Service

If any notice or other document is:

(a) Sent by post it will be deemed received on the first day (excluding weekends and public holidays) 
	after posting;

(b) Sent by facsimile or email and the sender’s facsimile or email machine produces a transmission 
	report indicating that the facsimile or email was sent to the addressee, the report will be prima facie 
	evidence that the facsimile or email was received by the addressee in a legible form at the time 
	indicated on that report; or

(c) Sent by courier and the courier obtains a receipt or records delivery on a courier run sheet, the receipt 
	or record of delivery on a courier run sheet will be prima facie evidence that the communication was 
	received by the addressee at the time indicated on the receipt or courier run sheet, or left at a 
	conspicuous place at the Trade Premises or is handed to a designated Person(s) nominated by the 
	Consent Holder then that shall be deemed to be service on, or delivery to the Consent Holder at that 
	time.

- NOTE - It should be verified that notice has been served on the correct Person.

6.6.3 	Signature

Any notice or document to be given, served or delivered shall be signed by an Authorized Officer.

33

6.7	Offences

Every Person or Consent Holder or owner or Occupier of Trade Premises who:

(a) Fails to comply with or acts in contravention of any provision of this bylaw;

- (b) Breaches the conditions of any Consent to discharge granted pursuant to this bylaw; or

(c) Fails to comply with a notice served under this bylaw,

commits an offence under s. 239 of the LGA, and is liable to a fine as specified in s. 242 of the LGA, or the issue of an Infringement notice under s. 245 of the LGA.

In all cases the WWA may recover costs associated with damage to the WWA Sewerage System and/ or breach of this bylaw in accordance with s. 175 and s. 176 of the LGA respectively.

6.8 Miscellaneous

All Businesses and industries operating within the Carterton District, and utilising neighbouring

Territorial Authorities water and waste water services shall comply with both these bylaws and the

bylaws of the neighbouring territorial authority.

34

APPENDIX A

- APPLICATION FOR TRADE WASTE DISCHARGE

(Normative)

THE WASTEWATER AUTHORITY OF THE Carterton District Council Logo APPLICATION FOR TRADE WASTE DISCHARGE

PLEASE PRINT CLEARLY

TRADE NAME AND STREET ADDRESS OF TRADE PREMISES

... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... .. Phone: ... . Fax: ... After hours contact: ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... .. Phone: ...

POSTAL ADDRESS OF CUSTOMER FOR CHARGING

Name: ... Address: ...

OWNER OF PREMISES (if different from above)

Name: ... Address: ...

TERM OF CONSENT SOUGHT

From: ... For a period of: 1 year  2 years  5 years Other (specify)

ADDRESS FOR SERVICE FOR FURTHER ENQUIRIES CONCERNING THIS APPLICATION

Name: ... ………………………………………………………………….. Address: ……………………………………………………………………. Phone:………………………………... Fax: ………………………….....

THIS APPLICATION RELATES TO:

 Proposed new discharge - An existing discharge for which no consent exists Current point or place of discharge: ............................................... - Renewal of a consent - Variation to an existing consent Nature of variation of discharge: ............................................... Use and attach additional sheets as required

VALUATION NUMBER

………………………………………………………………………………………

LOT NUMBER

………………………………………………………………………………………

DP NUMBER

……………………………………………………………………………………….

ARE THE PREMISES ALREADY CONNECTED TO PUBLIC SEWER?

 Yes  No

CONNECTIONS REQUIRED

Size: ... .. No.: ... Size: ... .. No.: ... Note - Minimum size 100 mm.

DESCRIPTION OF MAIN TRADE ACTIVITY

………………………………………………………………………………………… …………………………………………………………………………………………

DIAGRAM FOR CONNECTION LOCATION (Show distances from boundaries, kerbs, buildings)

35

SIGNATURE BLOCK

…………………………………………………................................................... (Full Name) ……………………………………………………………………………………… (Position) 1. I am duly authorized to make this application. 2. I believe that all the information contained in this application is true and correct. Signature: ………………………………………………………………………… Date: ………………………………………………………………………………..

FOR OFFICE USE ONLY

APPLICATION NUMBER

…………………………………………………………………………

APPLICATION RECEIVED AND CHECKED BY

Inspector/Clerk: ... Date: ………………….. Permitted  Controlled  Conditional 

PROPERTY LINK IDENTIFICATION NUMBER

…………………………………………………………………………

BUILDING CONSENT NUMBER

…………………………………………………………………………

TRADE WASTE CONSENT

Approved by: ... No.: ... Date: ...

APPLICATION FEE

$... GST $... Total $...

Cashier Receipt: .......................................................................

File No.: ... ……………………………………………………………

36

- APPENDIX B

- DESCRIPTION OF TRADE WASTE AND PREMISES

(Normative)

- DESCRIPTION OF TRADE WASTE AND PREMISES - PLEASE PRINT CLEARLY

| 1 GENERAL PREMISES 1.1 Trade name and street address ……………………………………………………………………………………… ……………………………………………………………………………………… Phone: …………………………….Fax: ............................................................ 1.2 Name and address of owner/occupier Name: ........................................................................................................... Address: ...................................................................................................... ……………………………………………………………………………………… 1.3 Contact for enquiries (if different from above) Name: ........................................................................................................... Address: ...................................................................................................... ……………………………………………………………………………………… 1.4 Total volume of wastes: Average daily volume m3 ………… Maximum volume in any 8 hr period m3 ………… Maximum daily volume m3 ………… Maximum flow L/sec……. Seasonal fluctuation (range) ... 1.5 General characteristics of wastes: TYPICAL RANGE Temperature (oC) …………. ………… BOD5 (mg/L) …………. ………… COD (mg/L) …………. ………… Suspended solids (mg/L) …………. ………… pH …………. ………… Oil and greases …………. ………… 1.6 The source of water used on the premises is: (a) from ... . Council .. m3/working day (b) from other sources (state source) .. m3/working day 1.7 The wastes do / do not, contain condensing water or storm water and the layout of drains on the premises is / is not, such as to reasonably exclude the possibility of such becoming mixed with trade wastes. 1.8 It is / is not proposed that domestic wastewater and trade waste should be discharged at the same point of discharge. 1.9 The proposed method for flow measurement is:  a permanent installation of suitable flow measuring equipment  based on water usage as measured by meter  other, (specify) ………………………………………………………………; 1.10 List any substances contained in Schedule 1A or 1B of the bylaw which are stored, used, or generated on the premises. …………………………………………………………………………….. …………………………………………………………………………….. ……………………………………………………………………………… ……………………………………………………………………………… Describe mitigation measures employed to prevent accidental spillages of these substances from entering the public sewer or storm water system. …………………………………………………………………………….. ……………………………………………………………………………. ……………………………………………………………………………. …………………………………………………………………………….. 1.11 Site plans of the premises are attached which clearly show the location of the following as appropriate:  process areas  flow measuring devices  trade waste drains  emergency spill devices  domestic waste-  open areas draining to water drains trade waste drains  stormwater drains  emergency spill containment  other, (specify) …………………………………….. Main trade waste pre-treatment systems  screens  pH control  flow balance  grease traps  chemical treatment  biological treatment 1.12 Detailed drawings and descriptions for the following are attached as appropriate:  pre-treatment systems  flow measuring devices  emergency spill containment  sampling points  method of flow meter calibration 1.13 An independent waste audit of the premises has / has not been carried out by: ………………………………………………………………………… 1.14 A Discharge Management Plan is / is not attached. 1.15 The Health and Safety Requirements and security arrangements for Wastewater Authority staff entering the premises are as follows (specify) …………………………………………………………………… ……………………………………………………………………………………. |  |
| --- | --- |

37

| 2. PROCESS (Use a separate page for each process and attach copies of typical analyses for wastewater from each separate process) 2.1 Process name and description: ……………………………………………………………………....................................................................................................... ………………………………………………………………………..……………………………………………………………..………… ……………………………………………………………………………………………………………………………………..………… | 2.3 Volume of wastewater Average daily volume: ... m3 Maximum daily volume: ... m3 Maximum flow: ... L/s 2.4 If batch discharges Quality: ... m3 Frequency: ... m3 Rate of Discharge: ... L/s |
| --- | --- |
| 2.2 Type of product processed: VALUE OR CONCENTRATION. FROM PROCESS; AT POINT OF DISCHARGE. TYPICAL; MAX; TYPICAL; MAX. ……………..... ……………..... ……………..... ……………..... …………….....……………..... …………….....; ……………..... ……………..... ……………..... ……………..... …………….....……………..... …………….....; ……………..... ……………..... ……………..... ……………..... …………….....……………..... …………….....; ……………..... ……………..... ……………..... ……………..... …………….....……………..... ……………........... ……………………………………………………………………...................................................................................................... ………………………………………………………………………………………………………………………………………………. …………………………………………………………………….…………………………………………………………………………. 2.5 The wastewater contains the following Characteristic which when mixed with other wastewaters and discharged from the premises, are near or in excess of the limits stipulated in Schedule 1B of the bylaw. (NOTE - The characteristics in table 1A.2 and table 1A.3 have a limit of zero unless approval for that particular characteristic is applied for.) …………………………………………………………………………………………………………………………………………………………………………. …………………………………………………………......................................................................................................................................................... ………………………………………………………………………………………………………………………………………………………………………….. …………………………………………………………………………………………………………………………………………………………………………… ……………………………………………………………………………………………………………………………………………………………………………. |
| 2.6 The following steps have been / will be taken to improve the trade process as part of a strategy of cleaner production: …………………………………………………………........................................................................................................................................................ …………………………………………………………………………………………………………………………………………………………………………… …………………………………………………………......................................................................................................................................................... ………………………………………………………………………………………………………………………………………………………………………….. …………………………………………………………………………………………………………………………………………………………………………… …………………………………………………………........................................................................................................................................................ …………………………………………………………………………………………………………………………………………………………………………… …………………………………………………………......................................................................................................................................................... ………………………………………………………………………………………………………………………………………………………………………….. …………………………………………………………………………………………………………………………………………………………………………… Date of improvements: ... ………………………….. |  |

38

- APPENDIX C

- APPLICATION FOR TEMPORARY DISCHARGE

(Normative)

THE WASTEWATER AUTHORITY OF THE Carterton District Council Logo APPLICATION FOR TRADE WASTE DISCHARGE

PLEASE PRINT CLEARLY

| APPLICANT |  |  |  | LIQUID WASTE |  |
| --- | --- | --- | --- | --- | --- |
| Name:... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... Company:... ... ... ... ... ... ... ... ... ... ... ... ... ... ... Address: .............................................................................. .............................................................................. Phone: ………………… Fax: …………………….. Applicant responsible for liquid waste  Transportation  Generation  Licensed transporter |  |  |  | Quantity: ... . m3 Source: ............................................................................. ………………………………………………………………… ………………………………………………………………… Process in which waste was produced:…………………. ……………………………………………………………….. ……………………………………………………………… ………………………………………………………………… |  |
| GENERATOR / TRANSPORTER OF LIQUID WASTE (Delete Applicant’s responsibility) |  |  | - General characteristics BOD5: ............................................................... mg /L COD: ……………………………………………… mg /L Suspended solids: ............................................... mg /L pH: ………………………………………………….. Oil and grease: .................................................... mg /L List any characteristics which are likely to be greater than 50 % of concentrations stipulated in Schedule 1A of the Trade Waste Bylaw. ……………………………………………………………… ………………………………………………………………… ………………………………………………………………… ………………………………………………………………… |  |  |
| Name:... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... ... Company:... ... ... ... ... ... ... ... ... ... ... ... ... ... ... Address: .............................................................................. .............................................................................. Phone: ………………… Fax: …………………… |  |  |  |  |  |
| APPLICATION SOUGHT FOR |  |  |  |  |  |
|  One discharge  A number of discharges of the same kind of liquid waste over a period of one year |  |  |  |  |  |

| PROPOSED FORM OF DISPOSAL |  | ANALYSIS |
| --- | --- | --- |
| ……………………………………………………. …………………………………………………… If from premises to public sewer, which is existing trade waste consent number?………………………………………… |  | (Check with Wastewater Authority whether this is required)  Appended  Not required |

| PROPOSED FORM OF DISPOSAL |  | DECLARATION |
| --- | --- | --- |
| Time: ……………………. Date: …………………….. |  | We hereby certify that the above liquid waste is accurately described Applicant:……………………………………………… Transporter / Generator …………………………………….………. |

- FOR OFFICE USE ONLY

APPLICATION NUMBER

…………………………………….……….

TEMPORARY DISCHARGE FEE

$ GST $ _____________ Total: _______________

APPLICATION

Received:…………………. Date: ……………. Discharge:  Approved  Not Approved By: …………………………… Date: ………………………….

Cashier Receipt:………………………………………………….

TEMPORARY DISCHARGE

If approved: Where discharged: :…………………..………….. Time and Date: …………………………………… If not approved: Where referred to: ………………………………………………………… …………………………………………………………

- File No: ………………………………………………….

40

- APPENDIX D

- MODEL TRADE WASTE CONSENT FORM

(Normative)

THE WASTEWATER AUTHORITY OF THE Carterton District Council CONSENT TO DISCHARGE TRADE WASTE TO THE PUBLIC SEWER Pursuant to the Carterton District Council Trade Waste Bylaw 2008

To:  ………………………………………………………………………………………………………………………

(Consent Holder trade name)

Address: …………………………………………………………………………………………………………………

(Street address of Trade Premises)

Phone:...	..                        Fax: ...................................................................................

Name: …………………………………………………………………………………………………………………….

(Contact name)

Address:..................................................................................................................................................................

(Address for charging and service of documents)

……………………………………………………………………………………………………………………………...

(Trade activity)

| - In response to, and in terms of, the information declared in your application of ... . to discharge Trade Waste from the above Premises, the Consent of the WWA is hereby given for the term and subject to the conditions set out below: - That this consent relates to a proposed new discharge / an existing non-consented discharge / renewal of a consent / variation to an existing consent - That this is a permitted / conditional consent. - That the provisions of the Carteton District Council Trade Waste Bylaw 2008 are complied with at all times. - That this consent is valid for a period of ……. Years and will expire on …………….. - That the Trade Waste discharged under this consent shall consist only of wastes from the following processes: …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… …………………………………………………… | ………………………………………………………………. ………………………………………………………………. ………………………………………………………………. ……………………………………………………………….. - That this consent is subject to the specific conditions set out in Schedule 1A which is attached For and on behalf of the WWA of the Carterton District Council Authorized Officer: Name:……………………………………………… Signature: ………………………………………….. Date: …………………………………………………. FOR OFFICE ONLY Consent No.: ……………………………………….. Application No.: …………………………………….. File No.: ……………………………………………... |
| --- | --- |

- SCHEDULE 1A

- PERMITTED DISCHARGE CHARACTERISTICS

- 1A.1 Introduction

- 1A.1.1

The nature and levels of the Characteristics of any Trade Waste discharged to the WWA system shall comply at all times with the following requirements, except where the nature and levels of such Characteristics are varied by the WWA as part of an Approval to discharge a Trade Waste.

NOTE - It is very important to refer to the Guideline tables for background reasons for Contaminant concentrations.

- 1A.1.2

The WWA shall take into consideration the combined effects of Trade Waste discharges and may make any modifications to the following acceptable Characteristics for individual discharges the WWA believes are appropriate.

- 1A.1.3

- An additional column in tables 1A.1, 1A.2 and 1A.3 for Mass Limits may be added as required.

- 1A.1.4

The nature and levels of any Characteristic may be varied to meet any new resource Consents or other legal requirements imposed on the WWA, refer to 3.9 of the bylaw.

- 1A.2 Physical characteristics

- 1A.2.1 Flow

(a) The 24 hour flow volume shall be less than 5 m3.

(b) The maximum instantaneous flow rate shall be less than 2.0 L/s.

- 1A.2.2 Temperature

The temperature shall not exceed 40 C.

- 1A.2.3 Solids

(a) Non-faecal gross solids shall have a maximum dimension which shall not exceed 15 mm.

(b) The suspended solids content of any Trade Waste shall have a Maximum Concentration which shall 
	not exceed 2000 g/m3.   For Significant Industry this may be reduced to 600 g/m3.

(c) The settleable solids content of any Trade Waste shall not exceed 50 ml/L.

(d) The total dissolved solids concentration in any Trade Waste shall be subject to the Approval of the 
	WWA having regard to the volume of the waste to be discharged, and the suitability of the drainage 
	system and the treatment plant to accept such waste.

(e) Fibrous, woven, or sheet film or any other materials which may adversely interfere with the free flow 
	of Sewage in the drainage system or treatment plant shall not be present.

- 1A.2.4 Oil and grease

(a) There shall be no free or floating layer.

42

(b) A Trade Waste with mineral oil, fat or grease unavoidably emulsified, which in the opinion of the WWA 
	is not biodegradable shall not exceed 200 g/m3 as petroleum ether extractable matter when the 
	emulsion is stable at a temperature of 15 C and when the emulsion is in contact with and diluted by 
	a factor of 10 by raw Sewage, throughout the range of pH 6.0 to pH 10.0.

(c) A Trade Waste with oil, fat or grease unavoidably emulsified, which in the opinion of the WWA is 
	biodegradable shall not exceed 500 g/m3 when the emulsion is stable at a temperature of 15 C and 
	when the emulsion is in contact with and diluted by a factor of 10 by raw Sewage throughout the range 
	of pH 4.5 to pH 10.0.

(d) Emulsified oil, fat or grease shall not exceed 100 g/m3 as petroleum ether extractable matter when 
	the emulsion is unstable at a temperature of 15 C and when the emulsion is in contact with and 
	diluted by a factor of 10 by raw Sewage throughout the range of pH 4.5 to pH 10.0.

- 1A.2.5 Solvents and other organic liquids

There shall be no free layer (whether floating or settled) of solvents or organic liquids.

- 1A.2.6 Emulsions of paint, latex, adhesive, rubber, plastic

(a) Where such emulsions are not treatable these may be discharged into the Sewer subject to the total 
	suspended solids not exceeding 1000 g/m3 or the concentration agreed with the WWA.

(b) The WWA may determine that the need exists for Pre-treatment of such emulsions if they consider 
	that Trade Waste containing emulsions unreasonably interferes with the operation of the WWA 
	treatment plant e.g. reduces % UVT (ultra violet transmission).

(c) Such emulsions of both treatable and non-treatable types, shall be discharged to the Sewer only at 
	a concentration and pH range that prevents coagulation and blockage at the mixing zone in the public 
	Sewer.

- 1A.2.7 Radioactivity

Radioactivity levels shall not exceed National Radiation Laboratory Guidelines.

- 1A.2.8 Colour

No waste shall have colour or colouring substance that causes the discharge to be coloured to the extent 
that it impairs wastewater treatment processes or compromises the treated Sewage discharge Consent.

- 1A.3 Chemical characteristics

- 1A.3.1 pH value

The pH shall be between 6.0 and 10.0 at all times.

- 1A.3.2 Organic strength

- 1A.3.2.1

The Biochemical Oxygen Demand (BOD5) of any waste may require to be restricted where the capacity for receiving and treating BOD5 is limited. A BOD5 restriction may be related to Mass Limits.

Where there is no WWA treatment system for organic removal the BOD5 shall not exceed 1000 g/m3.  For Significant Industry this may be reduced to 600 g/m3.

NOTE - For biological process inhibiting compounds see table 5 in the Guidelines for Sewerage Systems: Acceptance of Trade Wastes (industrial waste) 12.

43

- 1A.3.3 Maximum concentrations

The Maximum Concentrations permissible for the chemical Characteristics of an acceptable discharge are set out in table 1A.1, table 1A.2 and table 1A.3.

- Table 1A.1 - General chemical characteristics

(Mass limits may be imposed, refer to 4.2)

| Characteristic | Maximum concentration (g/m3) |
| --- | --- |
| MBAS (Methylene blue active substances) | 500 |
| Ammonia (measured as N) - free ammonia - ammonium salts | 50 200 |
| Kjeldahl nitrogen | 150 |
| Total phosphorus (as P) | 25 |
| Sulphate (measured as SO4) | 500 1500 (with good mixing) |
| Sulphite (measured as SO2) | 15 |
| Sulphide - as H2S on acidification | 5 |
| Chlorine (measured as Cl2) - free chlorine - hypochlorite | 3 30 |
| Dissolved aluminium | 100 |
| Dissolved iron | 100 |
| Boron (as B) | 25 |
| Bromine (as Br2) | 5 |
| Fluoride (as F) | 30 |
| Cyanide - weak acid dissociable (as CN) | 5 |

44

- Table 1A.2 - Heavy metals

(Mass limits may be imposed, refer to 4.2)

| Metal | Maximum concentration (g/m3) | Metal | Maximum concentration (g/m3) |
| --- | --- | --- | --- |
| Antimony | 10 | Manganese | 20 |
| Arsenic | 5 | Mercury | 0.05 |
| Barium | 10 | Molybdenum | 10 |
| Beryllium | 0.005 | Nickel | 10 |
| Cadmium | 0.5 | Selenium | 10 |
| Chromium | 5 | Silver | 2 |
| Cobalt | 10 | Thallium | 10 |
| Copper | 10 | Tin | 20 |
| Lead | 10 | Zinc | 10 |

Table 1A.3 - Organic compounds and pesticides

(Mass limits may be imposed, refer to 4.2)

| Compound | Maximum concentration (g/m3) |
| --- | --- |
| Formaldehyde (as HCHO) | 25 |
| Phenolic compounds (as phenols) excluding chlorinated phenols | 50 |
| Chlorinated phenols | 0.02 |
| Petroleum hydrocarbons | 30 |
| Halogenated aliphatic compounds | 1 |
| Monocyclic aromatic hydrocarbons | 5 |
| Polycyclic (or polynuclear) aromatic hydrocarbons (PAHs) | 0.05 |
| Halogenated aromatic hydrocarbons (HAHs) | 0.002 |
| Polychlorinated biphenyls (PCBs) | 0.002 |
| Polybrominated biphenyls (PBBs) | 0.002 each |
| Pesticides (general) (includes insecticides,herbicides,fungicides and excludes organophosphate, organochlorine and any pesticides not registered for use in New Zealand) | 0.2 in total |

45

- SCHEDULE 1B

- PROHIBITED CHARACTERISTICS

- 1B.1 Introduction

This schedule defines Prohibited Trade Wastes.

- 1B.2 Prohibited characteristics

- 1B.2.1

Any discharge has prohibited Characteristics if it has any solid liquid or gaseous matters or any combination or mixture of such matters which by themselves or in combination with any other matters will immediately or in the course of time:

(a) Interfere with the free flow of Sewage in the Sewerage System;

(b) Damage any part of the Sewerage System;

(c) In any way, directly or indirectly, cause the quality of the treated Sewage or residual Biosolids and 
	other solids from any Sewage treatment plant in the catchment to which the waste was discharged 
	to breach the conditions of a Consent issued under the Resource Management Act, or water right, 
	permit or other governing legislation;

(d) Prejudice the occupational health and safety risks faced by sewerage workers; 
(e) After treatment be toxic to fish, animals or plant life in the receiving waters;

(f)  Cause malodorous gases or substances to form which are of a nature or sufficient quantity to create 
	a public nuisance; or

(g) Have a colour or colouring substance that causes the discharge from any Sewage treatment plant 
	to receiving waters to be coloured.

- 1B.2.2

A discharge has prohibited Characteristics if it has any characteristic which exceeds the concentration or other limits specified in Schedule 1A unless specifically Approved for that particular Consent.

- 1B.2.3

A discharge has a prohibited Characteristic if it has any amount of:

(a) Harmful solids, including dry solid wastes and materials which combine with water to form a 
	cemented mass;

(b) Liquid, solid or gas which could be flammable or explosive in the wastes, including oil, fuel, solvents 
	(except as allowed for in Schedule 1A), calcium carbide, and any other material which is capable of 
	giving rise to fire or explosion hazards either spontaneously or in combination with Sewage;

(c) Asbestos;

(d) The following organo-metal compounds:

Tin (as tributyl and other organotin compounds); 
(e) Any organochlorine pesticides;

(f) Any Organophosphate pesticides

46

(f)  Genetic wastes, as follows:

All wastes that contain or are likely to contain material from a genetically modified organism that is not in accordance with an approval under the Hazardous Substances and New Organisms Act.  The material concerned may be from Premises where the genetic modification of any organism is conducted or where a genetically modified organism is processed;

(g) Any health care waste prohibited for discharge to a Sewerage System by NZS  4304 or any 
	pathological or histological wastes; or

(h) Radioactivity levels in excess of the National Radiation Laboratory Guidelines.

47

SCHEDULE 1C

- TRADE WASTE CHARGES

Fees and charges are set by Council resolution.  This may be done by the annual planning process, fee 
setting or a similar transparent public process in accordance with the Local Government Act (LGA).

In the following table the Council states what categories they will charge, or may charge, under the tenure of this bylaw.

NOTE - A wide range of categories has been provided in the following table to leave options open and promote awareness for future changes in the WWA’s Sewerage System requirements.

| A. Administrative Charges |  |  |
| --- | --- | --- |
| Category | Description | Rate (excl gst) |
| A1 Connection fee | Payable on application for connection to discharge | At Cost |
| A2 Compliance Monitoring | The cost of sampling and analysis of Trade Waste discharge | At Cost |
| A3 Disconnection Fee | Payable following a request for Disconnection from Sewage System | At Cost |
| A4 Trade Waste Application fee | Payable on an application for a Trade Waste discharge | Sml Business (1-5 staff) $100 Med Business (6-15 staff) $190 Lge Business (16+ staff) $370 |
| A5 Reinspection fee | Payable for each re-inspection visit by the WWA where a notice served under this Bylaw has not been complied with by the Trade Waste discharger | $80/hr |
| A6 Special rates for loan charges | Additional rates for servicing loans raised for the purposes of constructing or improving the sewage system | By Agreement |
| A7 Temporary Discharge fee | Payable prior to receipt of Temporary discharge | 480/hr plus $120/ m3 |
| A8 Annual Trade Waste Charges | An annual management fee for a Trade Waste discharge to cover the WWA’s costs associated with for example: (a) Administration; (b) General compliance monitoring; (c) General inspection of Trade Waste Premises; (d) Use of the Sewerage System. This charge may vary depending on the Trade Waste sector and category of the discharger. | Small Controlled $90 pa Conditional $220 pa Medium Controlled $360 pa Conditional $700 pa Large Controlled $800 pa Conditional $1500 pa |
| A9 Rebates for Trade Premises within the District | Reduction in fees is provided for in s. 150(2). Section 150(4) of the LGA states that the fees prescribed by the Council shall not provide for the Council to recover more than the reasonable cost incurred by the Council for the matter for which the fee is charged.In no event shall the resultant charge be less than the Council’s sewerage charge for the equivalent period. | Discretion of Council As calculated by council |
| A10 New or Additional Trade Premises | Pay the annual fees and a pro rata proportion of the various Trade Waste charges relative to flows and loads | As per charges in these tables |

48

- B: Trade Waste Charges

| Category | Description | Rate |
| --- | --- | --- |
| B1 Volume | Payment based on the volume charged | $0.21/ m3 |
| B2 Flow rate | Payment based on the flow rate discharged $/L/s | $0.00021/L/s |
| B3 Suspended solids | Payment based on the mass of suspended solids $/kg | $0.44/kg |
| B4 Organic loading | Biochemical oxygen demand or chemical oxygen demand $/kg | $0.49/kg |
| B5 Nitrogen | Payment based on the defined form(s) of nitrogen $/kg | $5.0/kg |
| B6 Phosphorous | Payment based on the defined form(s) of phosphorous $/kg | $10.0/ kg |
| B7 Metals | Payment based on the defined form(s) of the metal(s) $/kg | $0.0/kg |
| B8 Transmissivity | A charge based on the inhibiting nature of the Trade Waste to UV light used by the WWA’s disinfection process | $0.0/kg |
| B9 Screenable solids | Payment based on the mass of screenable solids $/kg | $0.0/kg |
| B10 Toxicity charge | Payment based on the defined form(s) of the toxic substance(s) $/kg and/or $/m3 | Not currently accepted by WWA |
| B11 Incentive rebate | A rebate for discharging materials beneficial to the WWA’s Sewerage System $/kg and/or $/m3 | $0.0/kg |
| B12 Depreciation | Operating cost related to capital and normally spread across the volume and mass charges | Refer B1 & B2 above |
| B13 Capital | Apportioned upfront or term commitment capital cost of specific infrastructure required to accommodate a conditional Consent | By agreement |

- C: Tankered Waste Charges

| C1 Tankered Wastes | Set as a fee(s) per tanker load, or as a fee(s) per cubic metre, dependent on Trade Waste category | $120/ m3 or Tonne(1000kg) |
| --- | --- | --- |
| C2 Toxicity | Payment based on the defined form(s) of the toxic substance(s) $/kg and/or $/m3 | Not currently accepted by WWA |

49